## Slide 1
  MT880-Meter, that meets your needs through high functionality and communication flexibility
Look into the future ….
Waleed Abd El-Hameed, MScEE
Product Technical Support manager
Waleed.hammed@iskraemeco.com.eg

## Slide 2
  Meter parts #1
Up / down scroll button
Two LEDs Active & Reactive
Communication module
Terminal cover
Meter SN.
LCD
IR optical interface (no power reading)
Billing reset button / CT & VT label
Sealing meter cover screw
terminal cover screw
Meter Antenna

## Slide 3
  Meter parts #2
Meter terminals
Mechanism for CM module install / de-install
Additional terminals (external supply, communication interface)
Inputs / outputs part
Additional voltage terminals
Antenna connector
Modem & communication status
Terminal cover opening sensor

## Slide 4: Wiring Diagram
Phase | Terminals |  | 
 | Current input | Current output | Voltage input
L1 | 1 | 3 | 2
L2 | 4 | 6 | 5
L3 | 7 | 9 | 8
N | 10 | 12 | -

## Slide 5: Wiring Diagram in series
1
2
3
4
5
6
7
8
9
N
1
2
3
4
5
6
7
8
9
N
Old meter
new meter

## Slide 6: Correct wiring connection
Stranded cables can be used with appropriate ferrules only

## Slide 7: SIM Card installation
1- pull (step 1) the releasing mechanism till the final position (step 2).
2- Module will move up for a few millimeters and it can be easily removed (step 3).

## Slide 8: SIM Card installation
1. SIM card holder is placed on the bottom side of communication module.
2. To insert the card, move SIM card locking mechanism down,
3. open holder and
4. gently insert the card.
5. Close it and lock mechanism pushing it up.

## Slide 9: SIM Card installation
1. move locking mechanism to the “middle” position, where arrows are aligned in the line (step 1),
2. carefully insert the module (step 2),
3. gently press the module down and move locking mechanism into the “locked” position (step 3).

## Slide 10: Meter Dimension

## Slide 11
  Meter parts - LCD
OBIS code
Information quadrant
Voltage & current presence (direction)
Cursors
Register value
Register units, different statuses

## Slide 12
  Correct installation procedure
  Actual connection state on the LCD
    Phase quadrants
    Voltage presence and rotation field
    Current presence and direction
    Load control state, battery state, 5A relay state, alarm presence
  Please fill the checklist
  Photo After installation